VIDEO INSPECTION
A. Provide equipment of highest quality with high performance capabilities, produced
by a manufacturer engaged in the research, development and manufacturing of
said equipment.

B. The video camera and equipment shall have a color monitor for field viewing and
shall be recorded in color on a USB drive. In addition, the camera shall be capable
of being articulated to view in the downward and sideward directions or have
multiple cameras to view downward and sideward simultaneously. The camera
shall have a built-in depth counter to monitor depth in the field and record depth
on the image. The monitor shall also indicate and record the date and time of the
inspection, as well as the Well ID.

C. The Contractor shall submit one (1) copy of the USB drive of the video inspection
to the City of Florence.
D. Video the complete well from the top of the ground to the bottom of the well.
E. Video in both directions, top to bottom and bottom to top.

TESTING
A. Test pump and metering equipment:

1. Well driller to field verify the existing well/pump(s) and equipment is
operational and suitable to complete the required testing.

2. Utilize existing valves or provide throttling devices so that the discharge may
be reduced as necessary.

3. Owner will provide electric power for running tests.

4. Provide necessary discharge piping of sufficient size and length to
discharge the water pumps to the street drainage ditch.

5. Location of water discharge during performance testing must not affect test
results or cause damage by flooding, erosion or aquatic life and vegetation
at the disposal site.

6. Furnish flow measuring equipment as required.
7. Water level indicating gauges or measuring equipment capable of
determining water level within ±1" shall be furnished.

8. Provide name of person conducting performance test.

B. Performance testing (yield and specified capacity):

1. Pumping for capacity test shall be for such period of time as it may take to
reach stabilization of the water level or 12 hours, whichever is the longer
period.
2. Whenever there is an interruption in pump operation for a period greater
than 1% of the elapsed pumping time, a suspension of the test shall be
made until the water level has recovered to the static level.
a. Restart pump test and run for the full test period.
8. Manual water level readings shall be taken according to the following
timetable.
a. Prior to startup of test (static water level)
b. After 30 seconds
c. One minute to 10 minutes: once every minute
d. Ten minutes to 120 minutes: once every 10 minutes
e. One hundred twenty minutes to 4 hours: once every 30 minutes
f. Four hours to 12 hours: once every hour
g. Twelve hours to shut down: once every 2 hours
h. Prior to shutdown of test.
i. At the beginning of each performance test and during each two (2)
hour reading, the Contractor shall measure and record the flow of
water in cubic meters per hour.
j. After the pump is shut off, the Contractor shall measure water-level
recovery at the same frequency as specified above for the pumping
phase.
k. For the start of any constant-rate test (first 120 minutes) and
shutdown (first 120 minutes), the Contractor shall provide two (2)
qualified individuals to measure and record the water level in the
pumping well and one other well selected by Engineer.
l. Contractor and City staff shall consider transport of water-quality
samples and laboratory holding-times in scheduling the
commencement of any performance pumping test.

C. Chemical analysis:
1. Near the end of the pumping test, analyze for temperature, pH, conductivity,
sulfide, dissolved oxygen (DO) and oxidation reduction potential (ORP) of
the water shall be taken immediately upon collection of the samples and
recorded on the sample container and on the driller's log.
2. Two (2) one-gallon water samples shall be collected from the test pump.
2. Deliver samples promptly (in no event more than 30 hours) to a SCDHEC approved laboratory for analysis.
3. From time of sampling to time of delivery, the samples shall be kept
refrigerated, but not frozen.
4. Analyze one sample for:
( 1) Alkalinity1,2
( 2) Aluminum1
( 3) Antimony
( 4) Arsenic
( 5) Barium
( 6) Bicarbonate1,2
( 7) Cadmium
( 8) Calcium Hardness
( 9) Chloride 1
(10) Chromium
(11) Coliform (Total)
(12) Color1
(13) Conductivity
(14) Copper3
(15) Corrosivity
(16) Cyanide
(17) Fluoride1
(18) Iron1
(19) Lead3
(20) Magnesium1,2
(21) Manganese1
(22) Mercury
(23) Nickel
(24) Nitrate
(25) Nitrite
(26) Odor
(27) pH1
(28) Potassium
(29) Selenium
(30) Silver1
(31) Sodium4
(32) Sulfate1
(33) Temperature1,2
(34) TOC
(35) TDS1
(35) Thallium
(36) Turbidity
(37) Zinc1
All parameters measured in mg/l except pH, Color, and Turbidity.
1 Secondary Limits.
2 Corrosivity characteristics. Water must be non-corrosive. Corrosivity determined
by LSI and AI.
3 Action Levels.
4 A concentration of sodium in drinking water up to 20 mg/l is compatible with a
sodium restricted diet of 500 mg per day sodium.
5 Unit of measure is million fibers / liter (longer than 10m).

D. Sand content testing:

1. Maximum acceptable sand content is 5 milligrams per liter (ppm).
2. Sand content shall be determined by averaging the results of 5 samples
collected at the following times during the final pumping test:
a. 15 minutes after start of the performance test;
b. After 1/4 of pumping period has elapsed;
c. After 1/2 of pumping period has elapsed;
d. After 3/4 of pumping period has elapsed; and
e. Near the end of the pumping test.
3. For each test, sand content and turbidity shall be measured. Each well shall
be pumped at the design rate of the well.
Well water shall be clear to the unaided eye and turbidity levels shall be less
than or equal to 1 NTU. Sand content shall not exceed 2 ppm at the design
pumping rate as measured with a Rossum Sand Tester